Collection of Water Samples and In-situ testing

A total of three batches of water samples were collected from the Meghna River at the Haria Intake, Sonargaon, Narayanganj. Sampling location was about 100 - 150 ft from the river bank water line. A cylindrical container was used to collect water from a depth of about one meter below the water surface to avoid the presence of floating impurities. Separate sampling bottles and containers were used for water samples for physical and chemical water quality analysis, bacteriological water quality analysis, metal concentration analysis (acidified sample using HNO3 acid), and process model studies. During each sampling, in-situ measurements were done for the dissolved oxygen, pH, temperature and turbidity of the water sample. Table 1 shows the locations, dates, time and weather conditions of the sample collection. All the samples except those for model studies were put into ice box and all the samples were transported to the Environmental Engineering Laboratory of the Department of Civil Engineering, BUET quickly for testing and model studies.

Table 1: Date, Time, Location and Weather Condition of Water Sample Collection.

| Sampling ID | Date of Collection | Time of Collection | Coordinates of Sample Location | Weather Condition |
| --- | --- | --- | --- | --- |
| First Sampling | 13 July, 2013 | 9:00 – 9:15 AM | N 23o39’30.6” E 90o37’48.2” | Sunny Day |
| Second Sampling | 24 August, 2013 | 9:55 – 10:10 AM | N 23o39’31.3” E 90o37’49.1” | Sunny Day |
| Third Sampling | 28 September, 2013 | 10:20 – 10:35 AM | N 23o39’32.3” E 90o37’50.7” | Cloudy Sky |

Analysis of Raw Water Samples

Detailed laboratory analysis has been conducted on the three collected water samples to determine the water quality and the extent of treatment required. The results of the in-situ and laboratory analysis of the three samples are presented in Table 2 along with Bangladesh Drinking Water Standard (ECR’ 97).

Table 2: Water Quality Test Results from Meghna River at Baidder Bazar Intake, Haria, Sonargaon, Narayanganj. Sampling conducted on 13th July, 2013 (First Sample); 24th August, 2013 (Second Sample); and 28th September, 2013 (Third Sample).

| Sl. No. | Water Quality Parameter | Unit | Concentration Present (First Sample) | Concentration Present (Second Sample) | Concentration Present (Third Sample) | Bangladesh Drinking Water Standard (ECR’ 97) |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | pH | - | 7.03 | 7.26 | 6.92 | 6.5-8.5 |
| 2 | Color (Apparent) | Pt-Co | 62.0 | 159.0 | 85.0 | 15 |
| 3 | Color (True) | Pt-Co | 13.0 | 19.0 | 15.0 | 15 |
| 4 | Turbidity | NTU | 6.87 | 17.1 | 13.0 | 10 |
| 5 | Total Hardness | mg/L as CaCO3 | 16.0 | 20.0 | 36.0 | 200-500 |
| 6 | Chloride (Cl-) | mg/L | 10.0 | 7.0 | 7.0 | 150-600 |
| 7 | Total Dissolved Solids (TDS) | mg/L | 35.0 | 20.0 | 27.0 | 1000 |
| 8 | Iron (Fe) | mg/L | 0.38 | 0.44 | 0.32 | 0.3-1.0 |
| 9 | Total Coliform (TC) | CFU/100 mL | 390 | 20 | 134 | 0 |
| 10 | Fecal Coliform (FC) | CFU/100 mL | 210 | 20 | 110 | 0 |
| 11 | Electrical Conductivity (EC) at 25oC | µS/cm | 58 | 53 | 68 | -- |
| 12 | Dissolved Oxygen (DO) | mg/L | 7.60 | 6.0 | 5.25 | 6 |
| 13 | Alkalinity | mg/L as CaCO3 | 21.0 | 25.0 | 30.0 | -- |
| 14 | Nitrate (NO3-N) | mg/L | 0.4 | 0.2 | 0.4 | 10 |
| 15 | Ammonium (NH4-N) | mg/L | 0.23 | 0.354 | 0.274 | 0.5 |
| 16 | Ammonia (NH3-N) | mg/L | 0.001 | 0.004 | 0.001 | -- |
| 17 | Phosphate (PO4) | mg/L | 0.067 | 0.081 | 0.121 | 6 |
| 18 | Sulfate (SO4) | mg/L | 8.6 | <7 | <7 | 400 |
| 19 | Total Suspended Solids (TSS) | mg/L | 11.0 | 13.0 | 24.0 | 10 |
| 20 | Temperature | oC | 30.2 | 30.3 | 30.8 | 20-30 |
| 21 | Chemical Oxygen Demand (COD) | mg/L | 8.0 | 7.0 | 8.5 | 4 |
| 22 | Biochemical Oxygen Demand (BOD5) | mg/L | 1.0 | 0.4 | 0.6 | 0.2 |
| 23 | Chlorophyll-a | µg/L | -- | 2.7 | 0.3 | -- |
| 24 | Lead (Pb) | mg/L | <0.01 | 0.034 | 0.032 | 0.05 |
| 25 | Cadmium (Cd) | mg/L | 0.002 | 0.002 | 0.001 | 0.005 |
| 26 | Chromium (Cr) | mg/L | 0.005 | 0.005 | 0.003 | 0.05 |
| 27 | Zinc (Zn) | mg/L | 0.051 | 0.028 | 0.017 | 5 |
| 28 | Mercury (Hg) | mg/L | <0.0001 | <0.0001 | <0.0001 | 0.001 |

For the first sample, the apparent color, fecal coliform, total coliform, total suspended solids, COD and BOD concentrations exceed the Bangladesh Drinking Water Standard. For the second sample, these parameters and in addition, the true color and turbidity do not satisfy the Standard. For the third sample, color (apparent), turbidity, iron, total coliform, fecal coliform, total suspended solids, COD and BOD concentrations exceed the Bangladesh Drinking Water Standard. Although the iron concentration of all the samples satisfies the upper limit of the Standard but is slightly higher than the lower limit. It is desirable that the iron concentration should be below the lower limit of the Standard. The temperatures of all the three samples were slightly above the highest acceptable limit according to Bangladesh Drinking Water Standard. However it is expected that after treatment the temperature of the water will drop in the distribution network and will be within the acceptable limit. Hence, the raw water is to be treated to remove all the impurities mentioned here to make it suitable for drinking purpose.